Pvlib-Service

Production Deployment Guide

Windforce Solar PV Power Prediction  ·  v1.0  ·  April 2026

This document is a complete step-by-step guide for the team that will host and operate the Pvlib-Service. It covers server provisioning, deployment, ThingsBoard configuration, service verification, monitoring, and the plant rollout schedule.

1. What This Service Does

The Pvlib-Service is a Python/FastAPI application that runs a physics-based solar power prediction model every minute. For each enabled plant it:

•  Fetches real weather station irradiance from ThingsBoard (Tier 1), falls back to Solcast API (Tier 2), then to a pvlib clear-sky model (Tier 3).

•  Runs a 9-step PVsyst loss chain (cell temperature, IAM, DC losses, inverter efficiency, AC wiring) using the pvlib library.

•  Writes the computed expected AC power back to ThingsBoard as potential_power (kW) and active_power_pvlib_kw (kW) on the plant asset — these feed existing dashboard widgets with zero widget changes required.

•  Rolls up power totals to parent aggregation assets (SCADA group, Windforce group, etc.) so portfolio-level widgets stay accurate.

| Repo | https://github.com/L0rd008/PV-Power-Prediction |
| --- | --- |
| Service folder | scripts/Pvlib-Service/ |
| TB host | https://windforce.thingsnode.cc |
| Write cadence | Every 1 minute |
| Primary output key | potential_power (kW) on each plant ASSET |
| Physics version | pvlib-h-a3-v1 |

2. Prerequisites

2.1  Server

•  EC2 t4g.small (ARM64, 2 vCPU, 2 GB RAM) — minimum recommended instance type.

•  Ubuntu 22.04 LTS (arm64). Other Debian-based distros also work.

•  Security group: inbound TCP 8002 from your monitoring IP, outbound HTTPS (443) unrestricted.

•  Elastic IP assigned so the TB watchdog URL stays stable.

2.2  Software (install once)

# Update system

sudo apt-get update && sudo apt-get upgrade -y

# Install Docker

curl -fsSL https://get.docker.com | sudo sh

sudo usermod -aG docker $USER   # log out and back in after this

# Install Docker Compose plugin

sudo apt-get install -y docker-compose-plugin

# Install Git

sudo apt-get install -y git

# Verify

docker --version          # Docker 24+

docker compose version    # Compose v2.20+

git --version

2.3  ThingsBoard credentials

You will need a ThingsBoard service-account user with:

•  Tenant Admin or a custom role that allows: reading asset attributes, reading device timeseries, writing asset timeseries.

•  The account's email and password to put in .env.

NOTE:  Do NOT use your personal TB admin login. Create a dedicated service account (e.g. pvlib-service@windforce.lk) so credentials can be rotated without affecting other users.

3. Deploy the Service

3.1  Clone (sparse checkout — service folder only)

The repository contains multiple services. Use sparse checkout to pull only scripts/Pvlib-Service, keeping the working directory small.

# On the EC2 server:

git clone --no-checkout --depth 1 \

https://github.com/L0rd008/PV-Power-Prediction.git \

pvlib-service

cd pvlib-service

git sparse-checkout init --cone

git sparse-checkout set scripts/Pvlib-Service

git checkout main

# Navigate into the service directory — all commands run from here

cd scripts/Pvlib-Service

ls   # should show: app/ Dockerfile docker-compose.yml requirements.txt .env.example

3.2  Create the .env file

Copy the example file and fill in real credentials. Never commit this file to Git.

cp .env.example .env

nano .env

Fill in these values (all others can stay at their defaults):

| TB_USERNAME | Email of the TB service account |
| --- | --- |
| TB_PASSWORD | Password of the TB service account |
| TB_HOST | `https://windforce.thingsnode.cc` (already set in example) |
| TB_ROOT_ASSET_IDS | Already pre-filled with all 3 root asset UUIDs — do not change |
| SOLCAST_API_KEY | Leave blank for now (clear-sky fallback used until Solcast key available) |
| LOG_LEVEL | `INFO` for production; use `DEBUG` only when troubleshooting |

NOTE:  TB_ROOT_ASSET_IDS is already set in .env.example with the correct UUIDs for SCADA Power Plants, Windforce Plants, and WindForce Rooftop. Only change this if the hierarchy roots change.

3.3  Build and start

# Build the Docker image (first build takes 5-10 min — downloading Python wheels)

docker compose build

# Start the service in the background

docker compose up -d

# Watch the logs (Ctrl+C to stop watching — service keeps running)

docker compose logs -f pvlib-service

Expected log output within 30 seconds:

pvlib-service  | pvlib-service starting (mode=pvlib, scheduler=true)

pvlib-service  | scheduler: started — interval 1 min, max_concurrent 5 plants

pvlib-service  | INFO:     Application startup complete.

3.4  Confirm the service is healthy

curl http://localhost:8002/health

Expected response:

{

"status": "ok",

"scheduler_enabled": true,

"last_cycle_finished_at": null,   <- null until first cycle completes

"total_cycles": 0

}

NOTE:  The health endpoint returns HTTP 200 (ok) on startup even before the first cycle. It returns HTTP 503 (degraded) only if the scheduler has not completed a cycle in more than 120 seconds — this is the stall-detection signal for monitoring.

4. ThingsBoard Configuration

4.1  Enable a plant (required before any output is written)

The service discovers plants dynamically. A plant is computed only when it has both of these SERVER_SCOPE attributes set on its asset:

isPlant    = true

pvlib_enabled = true

To enable Kebithigollewa Solar Park (the first plant to go live):

1.  Log in to ThingsBoard at https://windforce.thingsnode.cc

2.  Navigate to Assets → find "KSP_Plant" (Asset ID: 0e4b4070-50ff-11ef-b4ce-d5aee9e495ad)

3.  Open the asset → Attributes tab → SERVER_SCOPE

4.  Confirm isPlant = true is already present (add it if missing)

5.  Add new attribute: key = pvlib_enabled, value type = Boolean, value = true → Save

NOTE:  Plants without pvlib_enabled=true are silently skipped by the BFS discovery. Setting it to false (or deleting it) is the safe way to pause a plant without stopping the service.

4.2  Plant physics configuration (pvlib_config)

Each plant asset must have a pvlib_config SERVER_SCOPE attribute containing a JSON object with its physical parameters. KSP_Plant already has this configured. For new plants, the JSON structure is:

{

"plant_name": "Plant Display Name",

"location": {

"lat": 8.123, "lon": 80.456, "altitude_m": 100, "timezone": "Asia/Colombo"

},

"orientations": [

{ "name": "Main", "tilt": 15, "azimuth": 0, "module_count": 2000,

"use_measured_poa": true }

],

"module": { "area_m2": 2.58, "efficiency_stc": 0.224, "gamma_p": -0.0029 },

"inverter": { "ac_rating_kw": 5000, "flat_efficiency": 0.98 },

"losses": { "soiling": 0.03, "mismatch": 0.0215, "dc_wiring": 0.015,

"ac_wiring": 0.005, "far_shading": 0.99 },

"station": {

"ghi_key": "wstn1_horiz_irradiance",

"poa_key": "wstn1_tilted_irradiance",

"air_temp_key": "wstn1_temperature_ambient",

"wind_speed_key": "wstn1_wind_speed",

"freshness_minutes": 10

}

}

NOTE:  use_measured_poa: true means the POA pyranometer reading is used directly (most accurate). Set to false if only a GHI sensor is available — the service will compute POA via the Perez transposition model.

4.3  Weather station device relationship

The service auto-discovers the weather station device by walking the Contains relations on the plant asset. A device is recognised as a weather station if its name contains WSTN, WEATHER, or STATION (case-insensitive). The device must have a Contains relation from the plant asset in ThingsBoard.

Known weather stations:

| KSP_WSTN1 | da2617d0-1ea6-11f1-a954-a570b75cadc0 (KSP_Plant child) |
| --- | --- |
| SOU_WSTN | Add Contains relation from SOU_Plant when enabling that plant |
| SSK_WSTN | Add Contains relation from SSK_Plant when enabling that plant |

5. Verify the Service Is Writing Data

5.1  Check plant discovery

Hit the discover endpoint to confirm the service can find enabled plants:

curl http://localhost:8002/pvlib/discover

Expected response after enabling KSP_Plant:

{

"plant_count": 1,

"plants": [

{

"id": "0e4b4070-50ff-11ef-b4ce-d5aee9e495ad",

"name": "KSP_Plant",

"parent_count": 2,

"parent_ids": ["<SCADA_root_id>", "<Windforce_root_id>"]

}

]

}

5.2  Force a manual run

Trigger an immediate compute cycle (useful to test before the 1-minute scheduler fires):

curl -X POST http://localhost:8002/admin/run-now

Then check the logs:

docker compose logs --tail 20 pvlib-service

Look for a line like:

process_single_asset: wrote 2 records for 0e4b4070-... (source=tb_station)

scheduler: cycle complete in 3.2 s — 1 plants, 0 failed

5.3  Confirm in ThingsBoard

1.  Open KSP_Plant in ThingsBoard → Latest telemetry tab.

2.  You should see: potential_power (kW), active_power_pvlib_kw (kW), pvlib_data_source (tb_station / solcast / clearsky), pvlib_model_version (pvlib-h-a3-v1).

3.  The values should update every minute. During daylight the potential_power should be a positive kW value matching roughly what the plant is producing.

NOTE:  If potential_power shows 0.0 during daylight hours: check pvlib_data_source. If it shows clearsky the weather station data is stale or the station device relation is missing. If it shows tb_station and power is still 0, check the station sensor key names in pvlib_config match the actual telemetry keys on the device.

6. Monitoring

6.1  Health endpoint

The /health endpoint is the primary signal for the service being alive and cycling correctly.

| URL | http://<server-ip>:8002/health |
| --- | --- |
| HTTP 200 ok | Scheduler is running and completed a cycle within the last 120 s |
| HTTP 503 degraded | No cycle completed in > 120 s — service is stalled |
| Check interval | Recommended: every 2 minutes from TB rule chain or external monitor |

6.2  Prometheus metrics

Machine-readable metrics are available in Prometheus text format:

curl http://localhost:8002/metrics

pvlib_cycle_duration_seconds 3.214

pvlib_total_cycles_total 42

pvlib_total_failures_total 0

pvlib_last_cycle_plants 1

pvlib_last_cycle_failures 0

These can be scraped by a Prometheus instance or simply curl'd by a CloudWatch script.

6.3  Docker logs

# Live log stream

docker compose logs -f pvlib-service

# Last 50 lines

docker compose logs --tail 50 pvlib-service

# Filter for warnings/errors only

docker compose logs pvlib-service 2>&1 | grep -E 'WARNING|ERROR'

6.4  ThingsBoard rule chain watchdog (recommended)

Add a rule chain in ThingsBoard that pings /health every 5 minutes and fires an alarm if it gets a non-200 response or times out. This gives you an in-platform alert without needing external monitoring infrastructure.

1.  TB → Rule Chains → create new chain: pvlib_health_watchdog

2.  Add a Generator node: fires every 5 min, msg body = {}

3.  Add a REST API Call node: GET http://<server-ip>:8002/health, timeout 5000 ms

4.  Route the Failure output to a Create Alarm node: alarm type = PvlibServiceDown, severity = CRITICAL

5.  Route the Success output to a Script node that checks: msg.status === 'ok' — if false, also route to alarm.

6.5  Service restart policy

The docker-compose.yml sets restart: unless-stopped. The container will automatically restart after a crash or server reboot. Verify with:

docker ps   # STATUS should show 'Up X minutes (healthy)'

7. Plant Rollout Plan

Roll out gradually — validate each plant's output before enabling the next batch. The service handles any number of enabled plants automatically once pvlib_enabled=true is set.

Week 1 — KSP only (validation week)

•  Enable: KSP_Plant (0e4b4070-50ff-11ef-b4ce-d5aee9e495ad)

•  Weather station: KSP_WSTN1 — already has a Contains relation, keys configured.

•  Gate: During daylight, confirm potential_power tracks the actual active_power within ±15%. Check pvlib_data_source = tb_station.

Week 2 — SOU + SSK

•  Enable: SOU_Plant and SSK_Plant — set pvlib_enabled=true on each.

•  Confirm SOU_WSTN and SSK_WSTN devices have Contains relations from their respective plant assets.

•  Add station key mappings to each plant's pvlib_config attribute.

•  Gate: All three plants showing tb_station source in daylight.

Week 3 — Remaining plants

•  Enable remaining plants one at a time. Plants without weather stations will fall back to clearsky automatically.

•  For plants with only clear-sky, expected accuracy is ±20% of actual — acceptable for potential-power reference.

•  Gate: /pvlib/discover shows all enabled plants, no plants in error state.

Week 4 — Parent roll-ups

•  Verify parent aggregation assets (SCADA group, Windforce group) are receiving rolled-up potential_power values.

•  Check TB Latest Telemetry on each parent asset for potential_power and active_power_pvlib_kw.

•  Gate: Portfolio-level widgets show summed expected power matching sum of individual plant values.

8. Operations Reference

8.1  Common commands

| Start service | docker compose up -d |
| --- | --- |
| Stop service | docker compose down |
| Restart service | docker compose restart pvlib-service |
| View logs | docker compose logs -f pvlib-service |
| Pull latest code + rebuild | git pull && docker compose up -d --build |
| Force immediate cycle | curl -X POST http://localhost:8002/admin/run-now |
| List recent jobs | curl http://localhost:8002/pvlib/jobs |
| Check health | curl http://localhost:8002/health |
| Discover enabled plants | curl http://localhost:8002/pvlib/discover |

8.2  API endpoints

| GET /health | Service health + last cycle stats. Returns 503 if stalled. |
| --- | --- |
| GET /metrics | Prometheus-format metrics (cycle duration, totals, failures). |
| GET /pvlib/discover | BFS discovery dry-run — lists all pvlib_enabled plants found. |
| POST /pvlib/run-asset | Synchronous single-plant compute. Body: {asset_id, start?, end?} |
| POST /admin/run-now | Trigger an immediate fleet cycle (fire and forget). |
| POST /pvlib/start | Async fleet job for current 1-min window. Returns job_id. |
| POST /pvlib/start-with-date | Async fleet job for explicit date range (backfill). Returns job_id. |
| GET /pvlib/status/{job_id} | Poll job status by ID. |
| GET /pvlib/jobs | List all recent jobs. |

8.3  Telemetry keys written to ThingsBoard

| potential_power | AC power (kW) — primary key read by dashboard widgets |
| --- | --- |
| active_power_pvlib_kw | AC power (kW) — ops alias |
| total_generation_expected_kwh | Daily expected energy (kWh) — written at 01:00 UTC |
| pvlib_daily_energy_kwh | Daily energy ops alias |
| pvlib_data_source | tb_station ¦ solcast ¦ clearsky ¦ rollup |
| pvlib_model_version | pvlib-h-a3-v1 |
| ops_expected_unit | kW (unit label for widgets) |

NOTE:  All keys are written to ASSET SERVER_SCOPE. No existing dashboard widget reads active_power_pvlib_kw or pvlib_daily_energy_kwh — dual-write is zero-impact on current dashboards.

8.4  Environment variables

| TB_HOST | ThingsBoard base URL |
| --- | --- |
| TB_USERNAME | Service account email |
| TB_PASSWORD | Service account password |
| TB_ROOT_ASSET_IDS | Comma-separated root asset UUIDs for BFS discovery |
| SCHEDULER_ENABLED | true / false — enable/disable the 1-min auto cycle |
| SCHEDULER_INTERVAL_MINUTES | Cycle interval in minutes (default: 1) |
| READ_LAG_SECONDS | How far behind now to read station data (default: 30) |
| READ_WINDOW_SECONDS | Width of the read window in seconds (default: 90) |
| MAX_CONCURRENT_PLANTS | Max plants computed in parallel per cycle (default: 5) |
| SOLCAST_API_KEY | Optional — Solcast API key for Tier-2 data fallback |
| LOG_LEVEL | INFO / DEBUG / WARNING / ERROR |

9. Troubleshooting

No plants found by /pvlib/discover

•  Check pvlib_enabled=true and isPlant=true are set (SERVER_SCOPE) on the plant asset in TB.

•  Verify TB_ROOT_ASSET_IDS in .env contains the correct root UUIDs.

•  Check logs for: discover_plants: plant <id> skipped (pvlib_enabled=false/missing)

potential_power is 0 during daylight

•  Check pvlib_data_source in TB Latest Telemetry.

•  If clearsky: weather station data is stale or the device/relation is missing. Check the Contains relation between plant and station in TB.

•  If tb_station but power=0: check station key names in pvlib_config match actual telemetry keys on the device. Keys are case-sensitive.

•  If night-time zeroing is wrong: check the plant's timezone in pvlib_config.

Health returns 503 / degraded

•  The scheduler has not completed a cycle in > 120 seconds.

•  Check Docker logs for error messages in the last cycle.

•  Try: docker compose restart pvlib-service

•  If problem persists: check TB connectivity with curl -s https://windforce.thingsnode.cc/health from inside the container: docker exec pvlib-service curl -s https://windforce.thingsnode.cc/health

Cycle takes > 45 seconds (logged as WARNING)

•  Increase MAX_CONCURRENT_PLANTS in .env (default 5, try 8 or 10).

•  If on t4g.small and consistently slow, consider upgrading to t4g.medium.

•  Check if TB is slow: docker compose logs show high latency in TB API calls.

TB authentication errors (401)

•  Token expired mid-operation — the client auto-refreshes but may fail if TB is unreachable.

•  Verify TB_USERNAME and TB_PASSWORD are correct in .env: docker compose exec pvlib-service env | grep TB_

•  Restart the service to force a fresh login: docker compose restart pvlib-service

To pause a single plant without stopping the service

In ThingsBoard: set pvlib_enabled=false (or delete the attribute) on the plant asset. The next BFS cycle will simply skip that plant. No service restart needed.

Pvlib-Service Deployment Guide  ·  v1.0  ·  April 2026  ·  Windforce / MAGICBIT